## yıldırım
LİGHTNİNG RİSK ASSESSMENT
Environment Coefficient C1
C1 | 0.25 | Surrounded by structures or trees of the same height or higher
| 0.5 | Surrounded by smaller structures
| 1 | No other structures within a distance equal to the height
| 2 | Isolated on top of a hill
Structural Coefficient C2
C2 | Structure / Roof | Metallic | Common | Flammable
| Metallic | 0.5 | 1 | 2
| Common | 1 | 1 | 2.5
| Flammable | 2 | 2.5 | 3
Structural Coefficient C3
C3 | 0.5 | Non flammable
| 1 | Flammable
| 2 | Valuable or partially flammable
| 3 | High value, highly flammable, explosive
Structure Occupancy C4
C4 | 0.5 | Unoccupied
| 1 | Occupied
| 3 | Difficult evacuation
Lightning Consequences C5
C5 | 1 | Service continuity not required
| 5 | Service continuity required without consequences
| 10 | Consequences on the environment
EFFİCİENCY AND PROTECTİON
Efficiency | Active Lightning Protection Levels | Cage Size | Down conductor distance
E>0,98 | LEVEL1+ADD | 5x5 | 10
0,95<E<0,98 | LEVEL1 | 5x5 | 10
0,90<E<0,95 | LEVEL2 | 10x10 | 15
0,80<E<0,90 | LEVEL3 | 15x15 | 20
E<0 | LEVEL4 | 20x20 | 25
CALCULATION OF PROTECTION LEVEL
The Equivalent Collection Area of Structure | Maximum Length - L
Maximum Width - W
Maximum Height - H
DESCRİPTİON
FACTOR | Environment Coefficient C1 | 0.5 | Surrounded by smaller structures |  | 0
| Structural Coefficient C2 | 0.5 |  |  | 0
| Structural Coefficient C3 | 2 | Valuable or partially flammable |  | 0
| Structure Occupancy C4 | 1 | Occupied |  | 0
| Lightning Consequences C5 | 10 | Consequences on the environment |  | 0
|  |  | FORMULAS | DESCRİPTİON
FORMULAS | Ae= | 0 | Ae=LxW+6xHx(L+W)+9xπxH² | The Equivalent Collection Area of Structure
| Ng= | 2.8084 | Ng=0,04xNk^1,25 | Lightning Density
| Nd= | 0 | Nd=NgxAexC1x10^ -6 | Expected number of lightning to plants
| Nk= | 30 | Nk=30 | Annual Average Thunder Days(world map)
| C= | 10 | C=C2xC3xC4xC5
| Nc= | 0.00015 | Nc=1,5x10^ -3/C | NUMBER OF LIGHTNING STRIKE
| E= | #DIV/0! | E=1-(Nc/Nd) | EFFİCİENCY
RESULT
EFFİCİENCY | VALUE | PROTECTİON LEVEL | CAGE SİZE | Down conductor distance
E= | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!